## Calculator
Estimating Pressure Drop in Gas Pipelines
Contact: waynelandon13@gmail.com
inputs
results
Q (Flowrate, MMscfd) |  |  | 3
Q (Flowrate, Mcfd) |  |  | 633.2308 |  | at flowing conditions
T1 (Inlet Temperature, F) |  |  | 100
P1 (Inlet Pressure ,psia) |  |  | 75
L (length of pipe, ft) |  |  | 20000
D (pipeline inside diameter, in) |  |  | 6
D (pipeline inside diameter, ft) |  |  | 0.5
E (Pipeline efficiency ,fraction) |  |  | 0.92
ρ (vapor density, lb/ft3) |  |  | 0.058395 | <= calculated from Properties Tab
μ (dynamic viscosity, lbm/sec- ft) |  |  | 1.0618e-05 | <= from Properties Tab
f ( friction factor) |  |  | 0.014924 | <= calculated from friction factor equations below *2
v (velocity, ft/sec) |  |  | 37.3455
Re, Reynolds Number |  |  | 4107623979.208
ΔP, psi (Darcy-Weisbach) |  |  | 26.7728
ΔP/P (%) *1 |  |  | 35.7%
ΔP, psi (Weymouth) |  |  | 39.1632
ΔP, psi (Panhandle A) |  |  | 27.9324
ΔP, psi (Panhandle B) |  |  | 20.0719
*1 Darcy-Weisbach valid for ΔP/P < 40%
*2 Moody Chart below can also be used to estimate fricion factor
Darcy-Weisbach Equation
The pressure drop (ΔP) in a gas pipeline can be calculated using the formula:
ΔP = f*(L/D)*ρ*(v2)/9265
Where:
ΔP = pressure drop (psi)
f = Darcy-Weisbach friction factor (dimensionless) determined from Reynolds Number
L = length of the pipe (ft)
D =internal diameter of the pipe (ft)
ρ = density of the gas (lbs/ft³)
v = flow velocity of the gas (ft/s)
Reynolds Number
Re = ρ * ν * L / μ
= ρ * v2 / (μ * v / L)
= v * L / u
Where:
Re = Reynolds Number (non-dimensional)
ρ = density (lbm/ft3)
ν = velocity based on the actual cross section area of the duct or pipe (ft/s)
μ = dynamic viscosity (lbm/sec- ft)
L = characteristic length (ft)
u = μ / ρ = kinematic viscosity (ft2/s)
Friction Factor
Estimate Friction Factor via equation or Chart
[6 empty] | Re | f | e/D (steel)
| laminar flow (Re<2100) |  |  | f = 64/Re |  | 4107623979.208 | 1.5581e-08
| smooth pipe turbulent flow |  |  | f = 0.316/Re0.25 |  | 4107623979.208 | 0.0012482
| completely turbulent flow |  |  | f = [1.14+2log(D/e)]-2 |  | 4107623979.208 | 0.014924 | 0.0003
| Transition Region |  |  | f = {-2log[(e/D)/3.7+2.51/(Re*f0.5)]}-2 |  | 4107623979.208 | 0.014937 | 0.0003
|  | e (pipe roughness) |  | ft | mm | e/d
|  | e for plastic pipe |  | 5e-06 | 0.001524 | 1e-05
|  | e for steel pipe |  | 0.00015 | 0.04572 | 0.0003
|  | e for galvinized pipe |  | 0.0005 | 0.1524 | 0.001
|  | e for cast iron pipe |  | 0.00085 | 0.25908 | 0.0017
|  | e for concrete pipe |  | 0.0005 | 0.1524 | 0.001
[6 empty] | Re | f
| For non laminar flow using chart ======> |  |  |  | for smooth pipe | 4107623979.208 | 0.008
[5 empty] | for turbulent flow | 4107623979.208 | 0.013
Weymouth Correlation
P2 = {(P1)2 - (Le*G*Tf)*[Q/(433.59*(Tb/Pb)*D2.667)]2}0.5
P2 = | 35.8368 | psia
Panhandle A Equation
P2 = {(P1)2 - (Le*G0.8539*Z*Tf)*[Q/(435.27*E*(Tb/Pb)1.0788*D2.6182)]1/0.5394}0.5
P2 = | 47.0676 | psia
Panhandle B Equation
P2 = {(P1)2 - (Le*G0.951*Z*Tf)*[Q/(737*E*(Tb/Pb)1.02*D2.53)]1/0.51}0.5
P2 = | 54.9281 | psia
Nomenclature
Q, Flow Rate (ft3/day)
Tb, Temperature Base (520 °R)
Pb, Pressure Base (14.65 psia)
D, Internal Diameter (in)
P1, Upstream Pressure (psia)
P2, Downstream Pressure (psia)
G, Gas Specific Gravity
Le. Pipe Segment Length including Expansion (miles)
Tf, Gas Flowing Temperature (°R)
E, Pipeline Efficiency factor (.92 for wet gas, 0.98 for dry gas)
Z, Compressibility factor

## Discussion
Estimating Pressure Drop in Gas Pipelines using Darcy-Weisbach, Weymouth, Panhandle A and Panhandle B Correlations
Contact: waynelandon13@gmail.com
This worksheet uses various correlations to estimate the pressure drop in a natural gas pipeline.
Darcy-Weisbach correlation requires estimating the friction factor, either from equations or charts
The Weymouth, Panhandle A and Panhadle B correlations were derived similarly from experimental data - and thus have the same form.
The Properties tab provides an estimate for the gas density based on the composition of the gas
If needed, the Composition tab provides compositions for a variety of natural gas streams
Since most field gas pipelines are not single phase, the gas flow will need to be sufficient to move the liquid phase (or slugs).
Gas velocities around 100 ft/sec are a good starting point for providing sufficient velocities to move the liquid or slugs.
Very high velocities can cause erosion in the pipe. These are rules of thumbs and only provided as help in estimating pressure drop.
Example 1
Calculate pressure drop for a 5.2 GPM gas from a wellhead separator flowing at 3.5MMscfd into a 2 mile long, 8" ID steel pipeline at 80F and 100 psia
Q (Flowrate, MMscfd) | 3.5
T1 (Inlet Temperature, F) | 80
P1 (Inlet Pressure ,psia) | 100
L (length of pipe, ft) | 10560
D (pipeline inside diameter, ft) | 0.67
E (Pipeline efficiency ,fraction) | 0.92
ρ (vapor density, lb/ft3) | 0.058395
μ (dynamic viscosity, lbm/sec- ft) | 1.0618e-05
f ( friction factor) | 0.014038
v (velocity, ft/sec) | 17.5486
Re, Reynolds Number | 1019128136.9666
ΔP, psi (Darcy-Weisbach) | 2.9215
ΔP/P (%) | 2.922%
ΔP, psi (Weymouth) | 3.2029
ΔP, psi (Panhandle A) | 2.8305
ΔP, psi (Panhandle B) | 2.1255
ΔP, psi (DWSIM) | 2.1255 | Check using DWSIM process simulator with Lockart/Martinelli Correlation
Example 2
Calculate pressure drop for a 5.2 GPM gas from a wellhead separator flowing at 25MMscfd into a 10 mile long, 18" ID steel pipeline at 80F and 1000 psia
Q (Flowrate, MMscfd) | 25
T1 (Inlet Temperature, F) | 80
P1 (Inlet Pressure ,psia) | 1000
L (length of pipe, ft) | 52800
D (pipeline inside diameter, ft) | 1.5
E (Pipeline efficiency ,fraction) | 0.92
ρ (vapor density, lb/ft3) | 0.058395
μ (dynamic viscosity, lbm/sec- ft) | 1.0618e-05
f ( friction factor) | 0.01197
v (velocity, ft/sec) | 2.5008
Re, Reynolds Number | 726169239.1814
ΔP, psi (Darcy-Weisbach) | 1.1299
ΔP/P (%) *1 | 0.113%
ΔP, psi (Weymouth) | 1.0874
ΔP, psi (Panhandle A) | 1.0689
ΔP, psi (Panhandle B) | 0.9118
ΔP, psi (DWSIM) | 17.3 | Check using DWSIM process simulator with Lockart/Martinelli Correlation
The Weymouth, Panhandle A, and Panhandle B equations were developed to simulate compressible gas flow in long pipelines. The Weymouth is the oldest and most common of the three. It was developed in 1912. The Panhandle A was developed in the 1940s and Panhandle B in 1956 (GPSA, 1998). The equations were developed from the fundamental energy equation for compressible flow, but each has a special representation of the friction factor to allow the equations to be solved analytically. The Weymouth equation is the most common of the three - probably because it has been around the longes. The Panhandle equations include a pipeline efficiency factory which can be used to more closely model flow at lower flows and pressures. The equations were developed for turbulent flow in long pipelines. For low flows, low pressures, or short pipes, they may not be applicable.
If the pressure drop in a pipeline is less than 40% of inlet pressure and at lower flows and shorter pipeline lengths, the Darcy Weisbach Correlation may be more accurate than the Weymouth or Panhandles. The Darcy-Weisbach method is valid for any flow rate, diameter, and pipe length, but does not account for gas compressibility

## Properties
Properties of various components of natural gas
from GPSA Handbook
| Input | Or use data from Compositions tab
Standing F
| Comp |  |  | Boiling Pt | Vap Pres | Freezing Pt | Crit. Pres | Crit. Temp |  | Density of Liquid |  |  | Density in Vapor |  | Cp ,Gas | Cp. Liquid | HV, gas | HV, liq | GPM
| mol% | Formula | MW | F@1atm | psia@100F | F | psia | F | Z | Spec Grav | lb/gal | gal/lbmol | Spec Grav | ft3/lb | Btu/lb-F | Btu/lb-F | Btu/ft3 | Btu/lb | gals/Mcf | b (oR) | TB (oR) | F
Nitrogen | 1.2% | N2 | 28.013 | -297.332 |  | -346 | 493 | -232.7 | 0.99997 | 0.8094 | 6.748 | 4.1513 | 0.96697 | 13.5496 | 0.2484 |  |  |  |  | 470 | 109 | 3.2902
Carbon Dioxide | 5.558% | CO2 | 44.01 | -109.32 |  | -69.77 | 1071 | 87.87 | 0.9943 | 0.8176 | 6.8163 | 6.4566 | 1.5192 | 8.6245 | 0.199 |  |  |  |  | 652 | 194 | 1.9434
Hydrogen Sulfide | 0% | H2S | 34.076 | -76.56 | 387.1 | -121.58 | 1036 | 212.6 | 0.9903 | 0.7871 | 6.5621 | 5.1929 | 1.1763 | 11.1388 | 0.2379 | 0.4968 | 637 |  |  | 1136 | 331 | 0.96246
Methane | 74.84% | CH4 | 16.043 | -258.7 | 5000 | -296.5 | 667.8 | -116.68 | 0.9981 | 0.3 | 2.5011 | 6.4144 | 0.55378 | 23.6592 | 0.5266 |  | 1009.7 |  |  | 300 | 94 | 2.5393
Ethane | 10.37% | C2H6 | 30.7 | -127.44 | 800 | -297.04 | 707.8 | 90.1 | 0.9961 | 0.3563 | 2.9705 | 10.3351 | 1.0597 | 12.3637 | 0.408 | 0.9256 | 1768 | 65889 | 2.8229 | 1145 | 303 | 1.2897
Propane | 4.914% | C3H8 | 44.097 | -43.73 | 188 | -305.82 | 616.3 | 206.1 | 0.9808 | 0.5075 | 4.231 | 10.4223 | 1.5222 | 8.6075 | 0.3887 | 0.5902 | 2517 | 90962 | 1.3497 | 1799 | 416 | 0.41365
isoButane | 0.647% | C4H10 | 58.124 | 10.74 | 72.39 | -255.28 | 529.1 | 274.96 | 0.9661 | 0.563 | 4.6937 | 12.3833 | 2.0064 | 6.5303 | 0.3867 | 0.566 | 3252 | 98968 | 0.21111 | 2037 | 471 | -0.10342
nButane | 1.428% | C4H10 | 58.124 | 31.12 | 51.54 | -217.05 | 550.7 | 305.62 | 0.9367 | 0.5843 | 4.8713 | 11.9319 | 2.0064 | 6.5303 | 0.3951 | 0.566 | 3262 | 102918 | 0.44899 | 2153 | 491 | -0.29551
isoPentane | 0.3308% | C5H12 | 72.151 | 82.11 | 20.444 | -255.82 | 490.4 | 369.03 | 0.948 | 0.6244 | 5.2056 | 13.8602 | 2.4905 | 5.2607 | 0.3829 | 0.5353 | 4000 | 108722 | 0.12083 | 2368 | 542 | -0.77882
nPentane | 0.3462% | C5H12 | 72.151 | 96.91 | 15.575 | -201.51 | 488.6 | 385.6 | 0.942 | 0.6311 | 5.2615 | 13.7131 | 2.4905 | 5.2607 | 0.399 | 0.548 | 4008 | 110071 | 0.12509 | 2480 | 557 | -0.93888
C6 | 0.301% | C6H14 | 86.178 | 155.73 | 4.96 | -139.58 | 710.4 | 453.6 | 0.91 | 0.664 | 5.5358 | 15.5675 | 2.9747 | 4.4044 | 0.3857 | 0.5332 | 4756 | 115055 | 0.12349 | 2738 | 610 | -1.4636
C7+ | 0.04986% | C7H16 + | 100.2 | 176.16 | 3.225 | 41.96 | 710.4 | 552.22 | 0.929 | 0.8845 | 7.3741 | 13.5881 | 3.4588 | 3.7881 | 0.2422 | 0.4098 | 3741 | 132651 | 0.017854 | 2800 | 619 | -1.5635
Toluene | 0.01% | C7H8 | 92.14 | 231.13 | 1.003 | -138.98 | 595.5 | 605.57 | 0.903 | 0.8719 | 7.269 | 12.6757 | 3.1805 | 4.1194 | 0.2598 | 0.4009 | 4475 | 132659 | 0.0033401 | 3000 | 800 | -2.7717
Ethylbenzene | 0.006663% | C8H10 | 106.167 | 277.16 | 0.3716 | -138.96 | 523.4 | 651.29 | 0.9 | 0.8717 | 7.2674 | 14.6087 | 3.6647 | 3.5752 | 0.2795 | 0.4113 | 5222 | 134381 | 0.0025648 | 4200 | 850 | -4.1893
Xylene | 0.006663% | C8H10 | 106.16 | 291.97 | 0.2643 | -13.32 | 541.6 | 674.92 | 0.9 | 0.8847 | 7.3757 | 14.3931 | 3.6645 | 3.5754 | 0.2914 | 0.4161 | 5209 | 136036 | 0.0025269 | 4200 | 880 | -4.3577
Water | 0% | H20 | 18.015 | 212 | 0.9495 | 32 | 3207.9 | 705.5 | 0.3434 | 1 | 8.337 | 2.1608 | 0.62185 | 21.0694 | 0.4447 | 1.001 | 49 | 0 |  | 2000 | 400 | 0.65217
Stream (1) | 100% |  | 22.1647 | -216.8635 | 3835.2779 | -282.4546 | 686.0726 | -55.2697 | 0.99508 | 0.36042 | 3.0048 | 7.1931 | 0.76509 | 17.1247 | 0.48166 | 0.14227 | 1174.6297 | 14594.5986 | 5.2284
(1) weighted average
Dynamic viscosity | 1 cP = 0.0006719689 lb/(ft·s)
|  | cp | lb/(ft-s)
natural gas at 100 psi |  | 0.0147 | 9.879e-06
natural gas at 500 psi |  | 0.0151 | 1.0148e-05
natural gas at 1000 psi |  | 0.0158 | 1.0618e-05
Ave |  | 0.0152 | 1.0215e-05

## Compositions
Various Gas Compositions from Wellhead Separators
[5 empty] | Delaware Basin |  |  | EagleFord |  |  |  |  | Typical from Various Other Fields
Case ====> | 1 | 2 | 3 | 1 | 2 | 3 | Ave | 7 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Component | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol% | mol%
Nitrogen | 0.5% | 0.5% | 0.5% | 0.6055% | 1.487% | 1.506% | 1.199% | 0.07% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Carbon Dioxide | 2.5% | 2.5% | 2.5% | 0.154% | 6.29% | 10.23% | 5.558% | 1.37% | 2.5% | 3% | 3% | 3% | 3% | 3.2% | 3.3% | 3.3% | 3.3% | 3.4% | 3.5% | 3.4%
Hydrogen Sulfide | 0% | 0% | 0% | 0% | 0% | 0% | 0% | bar: EagleFord 7 to Typical from Various Other Fields 15
Methane | 87.25% | 87.7% | 88.1% | 80.17% | 71.81% | 72.53% | 74.84% | 69.4% | 88.47% | 83.2% | 84.13% | 84.35% | 83.2% | 82% | 80% | 79% | 77.5% | 75% | 73% | 70%
Ethane | 5.1% | 5.3% | 5.3% | 11.19% | 11.17% | 8.736% | 10.37% | 13.55% | 5.2% | 7.2% | 7.2% | 7.2% | 7.2% | 7.51% | 7.93% | 8.37% | 8.9% | 9.65% | 10.25% | 11.5%
Propane | 1.8% | 1.9% | 1.85% | 4.691% | 5.901% | 4.151% | 4.914% | 6.64% | 1.85% | 3.02% | 3.02% | 3.02% | 3.02% | 3.3% | 4.2% | 4.5% | 4.85% | 5.65% | 6.12% | 6.5%
isoButane | 0.4% | 0.2% | 0.15% | 0.762% | 0.722% | 0.4569% | 0.647% | 1.56% | 0.08% | 0.35% | 0.25% | 0.25% | 0.35% | 0.42% | 0.45% | 0.47% | 0.6% | 0.85% | 0.95% | 1.25%
nButane | 0.4% | 0.3% | 0.25% | 1.478% | 1.627% | 1.179% | 1.428% | 2.42% | 0.15% | 0.6% | 0.45% | 0.35% | 0.6% | 0.68% | 1.1% | 1.2% | 1.5% | 1.87% | 2.1% | 2.53%
isoPentane | 0.22% | 0.11% | 0.05% | 0.3415% | 0.361% | 0.29% | 0.3308% | 0.85% | 0.025% | 0.18% | 0.05% | 0.025% | 0.18% | 0.25% | 0.25% | 0.28% | 0.35% | 0.4% | 0.55% | 0.7%
nPentane | 0.4% | 0.2% | 0.1% | 0.338% | 0.357% | 0.3435% | 0.3462% | 0.69% | 0.05% | 0.35% | 0.1% | 0.05% | 0.35% | 0.4% | 0.58% | 0.632% | 0.75% | 0.85% | 1.1% | 1.5%
C6+ | 0.3% | 0.15% | 0.05% | 0.221% | 0.213% | 0.4691% | 0.301% | 1.1% | 0.025% | 0.4% | 0.1% | 0.05% | 0.4% | 0.5% | 0.45% | 0.47% | 0.47% | 0.55% | 0.65% | 0.8%
Benzene | 0.0375% | 0.0375% | 0.0375% | 0.0415% | 0.041% | 0.05709% | 0.04986% | 0.05% | 0.0375% | 0.05% | 0.05% | 0.05% | 0.05% | 0.06% | 0.06% | 0.07% | 0.07% | 0.07% | 0.07% | 0.08%
Toluene | 0.0375% | 0.0375% | 0.0375% | 0.012% | 0.051% | 0.03983% | 0.02094% | 0.05% | 0.0375% | 0.05% | 0.05% | 0.05% | 0.05% | 0.06% | 0.06% | 0.07% | 0.07% | 0.07% | 0.07% | 0.08%
Ethylbenzene | 0.0375% | 0.0375% | 0.0375% | 0% | 0.011% | 0.00219% | 0.00073% | 0.05% | 0.0375% | 0.05% | 0.05% | 0.05% | 0.05% | 0.06% | 0.06% | 0.07% | 0.07% | 0.07% | 0.07% | 0.08%
Xylene | 0.0375% | 0.0375% | 0.0375% | 0.001% | 0% | 0.006464% | 0.002488% | 0.05% | 0.0375% | 0.05% | 0.05% | 0.05% | 0.05% | 0.06% | 0.06% | 0.07% | 0.07% | 0.07% | 0.07% | 0.08%
Water | 1% | 1% | 1% | 0.001% | 0% | 0.006464% | 0.002488% | 2.15% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1%
Ave Stream | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Btu/cf | 1089 | 1070 | 1058 | 1238 | 1188 | 1095 | 1173.6667 | 1361 | 1051 | 1124 | 1096 | 1089 | 1124 | 1141 | 1170 | 1185 | 1210 | 1248 | 1282 | 1338
gals/Mcf | 2.54 | 2.35 | 2.2 | 5.4 | 5.8 | 4.5 | 5.2333 | 7.9 | 2.09 | 3.5 | 3.18 | 3.1 | 3.52 | 3.83 | 4.3 | 4.67 | 5.11 | 5.82 | 6.4 | 7.4
C6-C9 calc | 0.1378 | 0.067 | 0.022 | 0.38296 | 0.38296 | 56 | 51 |  | 0.01 | 0.186 | 0.044 | 0.02 | 0.18635 | 0.23505 | 0.20952 | 0.21922 | 0.21985 | 0.25852 | 0.30815 | 0.38296
C5+, mol% |  |  |  | 0.955% | 1.034% | 1.208% | 1.052% | 2.84% | 0.25% | 1.13% | 0.45% | 0.325% | 1.13% | 1.39% | 1.52% | 1.662% | 1.85% | 2.08% | 2.58% | 3.32%
CHDP, F | 60.18 | 43 | -1 | #REF! | #REF! | #REF! | #REF! |  | -21 | 97 | 27 | -2 | 97.858 | 209.828 | 139.0505 | 162.4766 | 164.1412 | 303.9279 | 618.1573 | 1479.0568

## Imperial units (hidden)
DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
THIS TOOL IS GIVEN ONLY TO ILLUSTRATE THE EXAMPLE DONE IN THE WEBSITE. USING IT FOR ANY OTHER PURPOSE IS AT OWN RISK OF USER
Gas expander available energy calculation |  |  | To modify | Calculated
This calculation sheet is allowing to estimate the amount of energy that a gas turbo expander could recover as well as the outlet temperature
Data input
| Gas conveyed |  | Natural Gas
| Molecular weight of the gas |  | 20 | g/mol
| Spefici gravity of gas vs air |  | 0.68966
| Gas viscosity |  | 0.0152
| Inlet temperature | T1 | 100 | F
|  |  | 559.67 | R
| Outlet temperature | T2 | 75 | F
|  |  | 534.67 | R
| Inlet pressure | P1’ | 75 | Psi abs
| Outlet pressure | P2 | 498.65 | Psi abs
| Total pipe length | Lm | 3.7879 | miles
| Pipe internal diameter | d | 6 | in
| Pipe roughness | epsilon | 0.00045 | mm
| Pipe elevation | DZ | 0 | ft
| Friction factor (Darcy) | f | 0.014924 |  | Please use abacus to determine the friction factor |  |  | You can also consider the following values
| Efficiency factor | E | 0.92 |  |  |  |  | Roughness | 0.00045 | mm
[9 empty] | 1.7717e-05 | in
| Average temperature | Tavg | 87.5 | F |  |  |  | d/epsilon | 338666.6558
|  |  | 547.17 | R |  |  |  |  | 12.1959
| Average pressure | Pavg | 338.9704 | Psi abs |  |  |  | Friction factor (Nikuradze) | 0.0067231
| Compressibility factor | Zf,avg | 1 |  | Please calculate Zf,avg separately |  |  | Friction factor Weymouth | 0.017621
| Potential energy term | phi | 0
| Absolute temperature at standard conditions | Tb | 520 | R
| Absolute pressure at standard conditions | Pb’ | 14.7 | Psi abs
|  | Tb/P’b | 35.3741
| (P1’)2-(P2’)2 – phi |  | -243026.8225
| f.Lm.Tavg.Zfavg.Sg |  | 21.3321
| Lm.Tavg.Zfavg.Sg |  | 1429.3887
| Lm.Tavg.Zfavg.Sg^0.8539 |  | 1509.1285
| Lm.Tavg.Zfavg.Sg^0.931 |  | 1466.509
| Calculation flow of compressible fluid in the pipeline |  |  |  | Re | f calculated | f assumed | Relative Difference
| Isothermal equation | q’h iso | #NUM! | scfh | #NUM! | #NUM! | 0.014924 | #NUM! | If the difference in between assumed and calculated is too big, put back the calculated value
| Weymouth equation | q’h wey | #NUM! | scfh |  |  |  |  | at the place of the assumed value above
| Panhandle A equation | q’h pan A | #NUM! | scfh
| Panhandle B equation | q’h pan B | #NUM! | scfh
If you spot a mistake or wish to suggest an improvement, please contact admin@powderprocess.net
Copyright www.PowderProcess.net
The content of PowderProcess.net is copyrighted but no warranty nor liability is ensured. The content of this site is to be seen as a help and important information and calculation must always be double checked by the user through the quality procedure of his organization or by checking another source. The user must always respect all applicable regulation. The use of the information is at the user and its organization own risk and own cost.
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN